CGApro with Box Matching and FFP Report

IRVING OIL

24" Light Crude Oil Pipeline - 24BUNKER

Dock #1 to Irving Oil Refinery

PROJECT NUMBER:	18338

REVISION No.:	0-1 (Draft)

REVISION DATE:	October 25, 2026

PREPARED BY:

Author		: Pending review

QA			: Pending review

Approver		: Pending review

© ROSEN GROUP 2026

CONFIDENTIALITY AND COPYRIGHT

This report (including any enclosures, attachments and digital deliverables) (the “Report”) has been prepared for the exclusive use and benefit of the addressee(s) and solely for the purpose for which it is provided. Nothing in this Report should be considered a guarantee or warranty of the correctness or completeness of data or conclusions contained herein. Unless ROSEN provides express prior written consent, no part of this Report should be reproduced, distributed or otherwise communicated to any third party. ROSEN does not accept any liability if this Report is used for an alternative purpose from which it is intended, nor shall ROSEN have any liability to any third party in respect of this Report. ROSEN collects data using various physical principles. ROSEN process this data in various ways to produce reports that include but are not limited to text, images, tables, listings, and graphs. The data processing ROSEN completes includes but is not limited to integration with other data, distance adaptation, noise filtering, interpolation, and calculations.

Executive Summary

This report summarises the available Box Matching and fitness-f
      or-purpose (FFP) evidence for pipeline 24BUNKER
      
      . The accompanying BM 
      Listing governs current inspection attributes; the pipe tally supplements missing information. Assumptions and unresolved conclusions are identified in red
      
      
      
      
       and explained in comments. Manual verification of the report is required prior to transmittal
      
      .

Metal Loss Immediate Integrity

The 2026 inspection summary reports no metal loss anomalies with an RSTRENG Effective Area failure pressure ratio of 1.0 or less. The 
      supp
      
      
      lied immediate FFP workbook states “No immediate repairs”. Final acceptance remains subject to confirmation of assessment inputs, tool tolerances and repair s
      
      tatus
      
      
      
      
      .

CGApro Results

No internal corrosion anomalies are reported in either 
      inspection. An internal corrosion growth rate is therefore not determined.

| Segment ID | Start Log Distance (m) | End Log Distance (m) | Recommended CGR (mm/year) |
| --- | --- | --- | --- |
| n/a | n/a | n/a | n/a |

For the illustr
      ative external corrosion screening scenario, one assumed rate is applied over the current corrosion population:

| Segment ID | Start Log Distance (m) | End Log Distance (m) | Recommended CGR (mm/year) |
| --- | --- | --- | --- |
| EC1* | 41.145 | 2,711.804 | 0.634* |

The assumed rate is the maximum positive historical rate in the Listing, 0.633646 mm/year (24.946709 mils/year). The recommended-rate column is unfilled; this assumption does not establish an approved corrosion-growth segment.

Of the 61 sized non-corrosion metal loss anomalies, 40 have saved previous matches and 21 are unmatched. The saved matching records do not establish whether the reported depth differences represent phys
      
      
      
      ical growth
      
      .

Metal Loss Future Integrity

Under the stated depth-limit scenario, 339 external corrosion anomalies reach 80% of wall thickness within five years of the 2026 ILI. This is an illustrative screening result, not a verified investigation or repair 
      schedule.

The earliest scenario crossing occur
      s 0.134 
      years after the ILI for Feature 5958, repor
      
      ted at 79% wt and log distance 1,503.851 m. A repair date cannot be assigned from this scenario alone.

Geometric Anomalies

The Listing contains 196 dents, of which 180 have saved previous matches and 16 are unmatched.

The maximum reported dent depth is 3.6% OD. The final static assessment decisions remain subject to confirmation of dent geometry, weld interacti
      on and damage class
      
      
      ification
      
      
      .

Dent fatigue lives have not been established from the supplied evidence.

Any fatigue conclusion will require a validated pressure history and dent stress or strain assessment, including confirmation of weld properties and associated cracking or gouging.

Laminations

Thirty laminations are reported. The screening workbook lacks the through-thickness inputs needed to validate its saved acceptance flags
      .

No verified lamination
      
      
       fatigue lives or fatigue-based repair dates are available.

Other Integrity Related Issues

The following recommendations distinguish reported observations from the additional evidence needed to complete the
      
       assessment.

Recommendations

Table 1: Recommended Actions

| Rehabilitation | Confirm the assessment inputs and the scenario assumptions before using Table 25 to support an investigation or repair progra mme . It would be prudent of Irving Oil to verify the repair status of any anomaly prior to undertaking any infield investigation. |
| --- | --- |
| Internal Corrosion | It is recommended that Irving Oil reassess the internal corrosion threat if there are any changes in operating conditions or the composition of the product. No internal corrosion population was reported; retain the normal corrosion monitoring programme. |
| External Corrosion | Review external corrosion growth together with coating, cathodic protection and repair information. |
| Geometric Anomalies | For any dents assessed as having a higher likelihood of external interference (e.g., TOL dents), the likelihood of associated gouging should also be evaluated by following this process: Consult records (i.e., surveillance reports, land access records) to determine if the dents are located in an area at risk from external interference. Perform a gouging susceptibility study using ILI signal data and other complementary data sets to categorise dents based on likelihood of gouging. Monitor dents where the risk of external interference is considered low. For dents located in areas at high risk from external interference or deemed likely to be associated with gouging, carry out a local targeted above-ground coating survey to determine the presence of any damage to the coating. The absence of coating damage would provide confidence that the dents are not associated with external interference/gouging. If coating damage is identified, the dents should be excavated in order to determine their origin and significance, and a suitable repair should then be installed if required. Confirm dent sharpness and complex geometry before assigning static assessment actions . The reported dent categories include 8 girth-weld dents and 33 seam-weld dents. Review construction or fabrication records to confirm whether the affected weld(s) are ductile or brittle. Repair any dent associated with a brittle weld. Complete strain assessment where verified geometry or the applicable acceptance c ri teria require it. C onfirm any associated metal loss, cracking or gouging before accepting the affected dents. No ovality anomalies are rep or ted in the 2026 summary; nine were reported in 2020. No wrinkles are identified in the suppli ed cu rr ent anomaly summary. C omplete fatigue assessment when a validated pressure history and dent assessment inputs are available. |
| Laminations | Obtain the missing lamination th rough-thickness dimens ions and confirm weld and metal loss interactions. For laminations associated with welds and/or major structural discontinuities (Table 23), Irving Oil should determine whether axial loading is a credible threat at the affected location(s). Where no credible axial loading threat exists, no further action is generally required. If axial loading is identified as a potential threat, a more detailed review of crossings, existing mitigation measures, and relevant geotechnical conditions may be necessary. Field investigations should be limited to those locations assessed as having the highest susceptibility. Do not assign lamination fatigue-based repair dates until the required assessments a re complete. |
| Other Integrity Related Issues | The tally record s 99 possible installations; their classification as close metal objects is not established . No eccentric casings are identified in the supplied summary. Confirm any casing records separately. Check the integrity of the casing end seals for evidence of water ingress. If possible, remove any water from the casing annulus and/or inert with corrosion inhibitors (typical inhibitors for use within a casing annulus are vapour inhibitors or gel inhibitors). Seal the casing ends preventing further water ingress. Monitor corrosion rates and review mitigation using validated inspection comparisons. Determine inspection timing from the completed engineering assessment. It is recommended that Irving Oil monitor areas in proximity to eccentric casings in future ILIs for any corrosion activity. C onfirm the construction and condition of the 21 reported patch installations before relying on their protection. Half shells and patches were permitted according to the applicable local pipeline code and any other regulations Appropriate qualified weld procedures were followed The absence of any defects was confirmed using Non-Destructive Testing (NDT). A Stress-Endurance (SN) fatigue assessment of the fillet welds has been conducted and demonstrated to have an acceptable fatigue life. - If construction, condition or compliance remains unresolved, determine appropriate inspection requirements. Any confirmed damage or cracking requires an eng ineering assessment and a verified repair design. No weld overlays are identified in the suppl ied summary. Review any confirmed closely spaced sleeves against applicable construction and assessment requirements. Repair records in relation to the closely spaced sleeves should be checked to confirm the presence of bridging sleeves. If a bridging sleeve has not been installed or this cannot be confirmed, Irving Oil should give due consideration to the cyclic loads due to axial, thermal and pressure cycling which may be present at the locations in order to determine the risk of crack growth due to the ‘notch-like’ condition. In those parts of the pipeline where the risk of crack growth is considered to be high due consideration should be given to the installation of a bridging sleeve. No mitre bends are identified in the supplied summary. Review records before classifying any tap as an illegal offtake; the supplied tally does not establish that classification. - The tally contains 72 taps; no illegal or suspicious offtake classification is established. |
| Reinspection | A safe reinspection interval is not established by the illustrative depth-limit scenario. Use suitable UT wall measurement and geometry inspection technologies for future comparisons, with compatible reporting and sizing specifications. If field findings or monitoring invalidate the scenario assumptions, review the growth-rate basis and repeat the relevant assessment before establishing a repair schedule or reinspection interval. |

Table of Contents

Executive Summary	2

Table of Contents	7

1	Pipeline Background	9

1.1	Pipeline Data	9

1.2	ILI Summary	9

1.3	ILI Findings	10

1.4	Summary of Repair Data	10

1.4.1	ILI Identified Repairs	11

1.4.2	Irving Oil Supplied Repair Data	11

1.4.3	Replacements	11

1.5	Operating Data Review	11

2	Data Review	13

2.1	Internal Corrosion	13

2.2	External Corrosion	13

2.3	Non-Corrosion Metal Loss	14

2.4	Geometric Anomalies	15

2.5	Laminations	16

3	ILI Comparison	18

3.1	CGApro with Box Matching & Signal Comparison	18

3.2	CGApro with AutoSCAN	19

3.3	Internal Corrosion	20

3.3.1	ILI Comparison: Box Matching & Signal Comparison	20

3.3.2	ILI Comparison: AutoSCAN	21

3.3.3	Recommended Corrosion Growth Rates	21

3.4	External Corrosion	23

3.4.1	ILI Comparison: Box Matching & Signal Comparison	23

3.4.2	ILI Comparison: AutoSCAN	24

3.4.3	Recommended Corrosion Growth Rates	24

3.5	Non-Corrosion Metal Loss	25

3.5.1	ILI Comparison: Box Matching and Signal Comparison	25

3.5.2	ILI Comparison: AutoSCAN	25

3.6	Geometric Anomalies	26

4	FFP Assessment Summary	27

4.1	Metal Loss Anomalies	27

4.2	Non-Metal Loss Anomalies	27

4.3	CSA Z662 Compliance Summary	27

5	Metal Loss Integrity Assessment	28

5.1	Immediate Integrity Assessment	28

5.2	Future Integrity Assessment	29

6	Geometric Integrity Assessment	31

6.1	Immediate Integrity Assessment	31

6.2	Fatigue Assessment	32

7	Lamination Integrity Assessment	34

7.1	Immediate Integrity Assessment	34

7.2	Crack Assessment	34

7.3	Fatigue Assessment	34

8	Other Integrity Related Issues	35

8.1	Close Metal Objects	35

8.2	Eccentric Casings	35

8.3	Half Sleeves / Patch Repairs	35

8.4	Weld Overlays	36

8.5	Closely Spaced Sleeves	36

8.6	Mitre Bends	36

8.7	Illegal Offtakes	37

9	Integrity Management Summary	38

9.1	Mitigation Strategy	38

9.1.1	Internal Corrosion	38

9.1.2	External Corrosion	38

9.2	Repair Plan	38

9.2.1	Sectional Repair Plan	39

9.3	Reinspection and Reassessment	40

10	References	41

Appendix A	Scope of Work	42

# Pipeline Background

This section summarises the supplied pipeline details, inspection history and reported installations. Current inspection information is taken from the 2026 final inspection rep
      ort [3] and its pipeline questionnaire [4]; the previous inspection is described in [5]
      .

## Pipeline Data

Table 2: Pipeline Details [3] [4]

| ROSEN Line Reference | 24BUNKER |
| --- | --- |
| Nominal Diameter | 24 in |
| Launcher | Dock #1 |
| Receiver | Irving Oil Refinery |
| Inspected Length | 2,714.588 m |
| Pipe Type | Longitudinal seam / seamless |
| Nominal Wall Thickness | 6.350 / 9.525 mm |
| Pipe Grade | API 5L X60 |
| Product | Light crude oil |
| Assessment Pressure | 23.166 bar (336 psi) |
| Assessment Temperature | 26 °C* |
| Construction Year | 1979 |

## ILI Summary

The assessments are based on the ILI data for the pipeline [3] [5]; details are provided in Table 3.

Table 3: ILI Details

|  | Recent ILI | Previous ILI |
| --- | --- | --- |
| Vendor | ROSEN | ROSEN |
| Date | May 21, 2026 | October 7–8, 2020 |
| Tool | UTWM / RoGeo XT / IMU | UTWM / RoGeo XT / Gyro |

Both inspection reports p
          rovid
      
      e data quality statements. Table 4 records the limitations relevant to comparing the supplied data; detailed qualification remains in the respective inspection reports [3] [5].

Table 4: Data Quality Summary

| Run Date | ILI Tool | Status | Comment |
| --- | --- | --- | --- |
| May 21, 2026 | UTWM / Geometry | Usable; limitations | UT data loss: 1.93%, including full circumferential loss at 142.790–302.833 ft. Geometry coverage: 100%. |
| October 7–8, 2020 | UTWM / Geometry / Gyro | Usable; limitati ons | UT coverage reported acceptable. Geometry run 1: full XGP coverage, 36.5% gyro loss. Run 2: 1.87% XGP loss, 3.82% gyro loss. |

The 2026 report notes reduced sizing accuracy for metal loss dimensions below 0.79 in and limitations at low remaining wall thickness. Confirm the treatment of sizing tolerance in the final assessment; the illustrative depth-limit scenario uses reported depths without an added tolerance
      
      .

## ILI Findings

A summary of the anomalies reported by the 2026 & 2020 ILIs is provided in Table 5.

Table 5: Summary of ILI Findings

| Anomaly Type |  | 2026 ROSEN UTWM / GEO |  | 2020 ROSEN UTWM / GEO |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | Number Reported | Maximum Reported Depth |  | Number Reported | Maximum Reported Depth |
| Internal Corrosion |  | 0 | n/a |  | 0 | n/a |
| External Corrosion |  | 8,331 | 79% wt |  | 4,786 | 79% wt |
| Pipe Mill Anomaly |  | — | — |  | — | — |
| Non-corrosion metal loss |  | 61 | 34% wt |  | 42 | 20–39% wt* |
| Longitudinal Weld Anomaly |  | — | — |  | — | — |
| Spiral Weld Anomaly |  | — | — |  | — | — |
| Girth Weld Anomaly |  | — | — |  | — | — |
| Other Anomaly |  | — | — |  | — | — |
| Repaired Anomaly |  | — | — |  | — | — |
| Dents (all types) |  | 196 | 3.6% OD |  | 186 | — |
| Complex Dent |  | — | — |  | — | — |
| Kinked Dent |  | — | — |  | — | — |
| ID Anomaly |  | 0 | n/a |  | 1 | — |
| Ovality |  | 0 | n/a |  | 9 | — |
| Wrinkle / Ripple |  | 0 | n/a |  | — | — |
| Lamination |  | 30 | n/a |  | 1 | n/a |
| Close Metal Object |  | — | — |  | — | — |
| Eccentric Casing |  | 0 | — |  | — | — |
| Half Sleeve / Patch Repair |  | 21* | — |  | — | — |
| Weld Overlay |  | 0 | — |  | — | — |
| Closely Spaced Sleeve |  | — | — |  | — | — |
| Mitre Bend |  | 0 | — |  | — | — |
| Illegal Offtake |  | 0 | — |  | — | — |
| Other unsized indications |  | 6 | n/a |  | 17 | n/a |
| Total anomalies* |  | 8,624 | — |  | 5,042 | — |
| Notes | Notes: “—” means not separately established. Totals include metal loss, deformations, laminations and other unsized indications; installations are excluded. The 2020 dent total is 183 plain dents plus 3 dents with metal loss. The previous non-corrosion maximum is known only to lie in the reported 20–39% wt band. Patch count denotes installations, not affected anomalies. |  |  |  |  |  |
|  | No internal corrosion anomalies are reported in the current or previous inspection summ aries . |  |  |  |  |  |

## Summary of Repair Data

The current tally identifies 21 patch installations and 36 start/end sleeve pairs. Reported installation presence does not establish repair adequacy
      
      
      
      . 
      
      
      
      C
      
      onfirm the repair status of affected anomalies before planning field work.

### ILI Identified Repairs

The 2026 inspection summary identifies both 79% wt corrosion anomalies, at 3,051.093 ft
      
       and 4,933.893 ft, as under patches
      .

### Irving Oil Supplied Repair Data

No separate client repair register was supplied for reconciliatio
      
      
      n in Table 6.

Table 6: Correlated Irving Oil Repair Data

| Irving Oil Reference | Irving Oil Distance (m) | Correlated ILI Log Distance (m) | Comment |
| --- | --- | --- | --- |
| — | — | — | — |
| — | — | — | — |
| — | — | — | — |

### Replacements

No replacement register was supplied for Table 7.

Table 7: Replacement Summary

| Start Log Distance (m) | End Log Distance (m) | Length of Replacement (m) | Number of Reported Anomalies (Deepest) |
| --- | --- | --- | --- |
| — | — | — | — |
| — | — | — | — |
| — | — | — | — |

## Operating Data Review

No pressure time series was identified in the supplied files. Nominal operating and assessment pressures are available, but these do not establish pressure-cycle history
      
      .

Figure 1 identifies the pressure-history information still required for fatigue analysis.

Figure 1: Pressure Monitoring Data

# Data Review

## Internal Corrosion

The 2026 and 2020 inspection summaries report no internal corrosion anomalies.

Figure 2 records the absence of a reported internal corrosion population.

Figure 2: Internal Corrosion, Depth, Orientation & Elevation vs. Log Distance

No internal corrosion growth rate is inferred from the absence of reported anomalies.

## External Corrosion

The Listing contains 8,331 external corrosion anomalies. The maximum reported depth is 79% wt, at log distances 929.973 m and 1,503.851 m (Features 957 and 5958).

The distribution of reported external corrosion anomalies is shown in Figure 3, with respect to depth, orientation and pipeline elevation.

Figure 3: External Corrosion, Depth, Orientation & Elevation vs. Log Distance

Figure 3 presents the supplied external corrosion depth, orientation and elevation distribution. Native chart distances are in miles.

## Non-Corrosion Metal Loss

The Listing contains 61 sized non-corrosion metal loss anomalies; the maximum reported depth is 34% wt.

The deepest sized non-corrosion anomaly is Feature 9055, at log distance 2,489.367 m.

Two additional manufacturing indications are unsized and are excluded from the sized population in Figure 4.

The distribution of reported non-corrosion metal loss anomalies is shown in Figure 4, with respect to depth, orientation and nominal wall thickness.

Figure 4: Non-Corrosion Metal Loss Anomalies; Depth, Orientation & Nominal Wall Thickness vs. Log Distance

Figure 4 shows the 61 sized non-corrosion anomalies and the supplied nominal wall thickness profile.

## Geometric Anomalies

The current Listing contains 196 dents: 155 reported as dents, 8 as girth-weld dents and 33 as seam-weld dents.

The deepest dent, Feature 7838, is reported at 3.6% OD and 7,307.854 ft in the tally, corresponding to 2,227.434 m. The Listing distance is interpreted as metres for this dent.

Figure 5 presents the native geometry chart, including geometric-
      centre orientation and elevation.

Figure 5: Geometric Anomalies; Centre Orientation & Elevation vs. Log Distance

The distribution chart does not establish static or fatigue acceptance.

## Laminations

Thirty laminations are reported. Figure 6 shows their distribution; final assessment classifications require the missing through-thickness dim
      en
      
      sions.

The distribution of reported laminations is shown in Figure 6, with respect to orientation and elevation.

Figure 6: Laminations; Orientation & Elevation vs. Log Distance

# ILI Comparison

## CGApro with Box Matching & Signal Comparison

The supplied BM Listing records saved current-to-previous matches. B
      ox matching estab
      lishes the reported associations; raw signal comparison evidence was not
       supplied.

Variations in reported anomaly counts and depths between repeat ILI runs may be related to real change due to corrosion growth over the inspection interval, however, variations may also arise due to differences in; run conditions, tool performance, inspection technology, data processing and repairs.

Table 8 and Figure 7 compare the complete reported metal loss populations. Figure 8 presents the full current Listing and the available previous matched subset on separate distance axes.

Table 8: Summary of Key ILI Metrics

| Value | 2026 ILI | 2020 ILI |
| --- | --- | --- |
| No. Individual Metal Loss Anomalies Reported | 8,392 | 4,828 |
| Maximum Reported Depth | 79% wt | 79% wt |
| Reporting Threshold | 10% wt | 10% wt |

Figure 7: Comparison of Reported Anomaly Depths; Anomaly Frequency vs. Depth

Figure 8: Current Metal Loss and Previous Matched Subset on Separate Distance Axes

## CGApro with AutoSCAN

AutoSCAN analysis is outside the selected Box Matching with FFP scope.

## Internal Corrosion

### ILI Comparison: Box Matching & Signal Comparison

No internal corro
      sion population is reported; no internal signal-comparison classifications or
      
      
      
       CGRs are applicable.

Table 9: Summary of Internal Corrosion ILI Comparison Results

| Result | Number of Anomalies | Maximum CGR |
| --- | --- | --- |
| Box Matching Only: |  |  |
| Matched | 0 | n/a |
| Unmatched | 0 | n/a |
| Signal Comparison: |  |  |
| New Growth | 0 | n/a |
| Existing Growth | 0 | n/a |
| Possible Growth | 0 | n/a |
| No Clear Growth | 0 | n/a |
| Inconclusive | 0 | n/a |
| Total | 0 | n/a |

An internal corrosion signal-comparison example is not applicable to this reported population.

Figure 9:
      
       Internal Corrosion Signal Comparison — Not Applicable

### ILI Comparison: AutoSCAN

AutoSCAN was not included in the selected scope; Table 10 is not applicable
      
      
      .

Table 10: Summary of Internal Corrosion ILI Comparison Results

| Result | Number of Anomalies | Maximum CGR |
| --- | --- | --- |
| New | n/a | n/a |
| Matched | n/a | n/a |
| Others | n/a | n/a |
| Total | n/a | n/a |

### Recommended Corrosion Growth Rates

#### Selection of Representative Anomalies

No representative internal corrosion
      
      
      
      
      
      
      
      
      
      
      
      
      
      
       anomalies are available for segmentation
      
      
      .

#### Segmentation Results

No internal corrosion segments or recommended rate
      
      
      
      
          
      s are ass
      ign
      
      ed
      .

Figure 10: Internal Corrosion Segmentation; CGR vs. Log Distance

Table 11: Internal Corrosion Segmentation Results

| Segment ID | Start Log Distance (m) | End Log Distance (m) | Recommended CGR (mm/year) |
| --- | --- | --- | --- |
| n/a | n/a | n/a | n/a |

Table 12: Internal Corrosion Anomalies, Details of Outliers

| Anomaly ID | Log Distance (m) | Joint No. | Orientation (hh:mm) | Depth (% wt) | Individual CGR (mm/year) |
| --- | --- | --- | --- | --- | --- |
| — | — | — | — | — | — |
| — | — | — | — | — | — |
| — | — | — | — | — | — |

## External Corrosion

### ILI Comparison: Box Matching & Signal Comparison

Of 8,331 external corrosion anomalies, 7,519 have saved previous matches and 812 are unmatched. Historical CGRs are numeric for 6,703 records and unavailable for 1,628. Signal-level growth classes are not established.

Table 13: Summary of External Corrosion ILI Comparison Results

| Result | Number of Anomalies | Maximum CGR |
| --- | --- | --- |
| Box Matching Only: |  |  |
| Matched | 7,519 | 24.9467 mils/year |
| Unmatched | 812 | — |
| Signal Comparison: |  |  |
| New Growth | — | — |
| Existing Growth | — | — |
| Possible Growth | — | — |
| No Clear Growth | — | — |
| Inconclusive | — | — |
| Total | 8,331 | 24.9467 mils/year |

Paired raw external corrosion signal images were not supplied. Figure 11 identifies this miss
      ing input.

Figure 11: External Corrosion Signal Comparison — Input Required

### ILI Comparison: AutoSCAN

AutoSCAN was not included in the selected scope; Table 14 is not applicable
      .

Table 14: Summary of External Corrosion ILI Comparison Results

| Result | Number of Anomalies | Maximum CGR |
| --- | --- | --- |
| New | n/a | n/a |
| Matched | n/a | n/a |
| Others | n/a | n/a |
| Total | n/a | n/a |

### Recommended Corrosion Growth Rates

#### Selection of Representative Anomalies

All 8,331 current corrosion records are retained. Figure 12 plots the 6,703 numeric historical CGRs: 4,330 negativ
      
      
      e and 2,373 positive. The 1,628 nonnumeric rates are not treated as zero
      
      
      .

#### Segmentation Results

The Listing contains no approved recommended segment rate. For the illustrative depth-limit scenario, the maximum positive historical rate is applied over the current corrosion population
      
      .

Figure 12: Saved Historical External Corrosion CGRs and Frequency Distribution

Table 15: Assumed External Corrosion Screening Segment

| Segment ID | Start Log Distance (m) | End Log Distance (m) | Recommended CGR (mm/year) |
| --- | --- | --- | --- |
| EC1* | 41.145 | 2,711.804 | 0.634* |

Table 16: External Corrosion Outliers — Selection Not Established

| Anomaly ID | Log Distance (m) | Joint No. | Orientation (hh:mm) | Depth (% wt) | Individual CGR (mm/year) |
| --- | --- | --- | --- | --- | --- |
| — | — | — | — | — | — |
| — | — | — | — | — | — |
| — | — | — | — | — | — |

## Non-Corrosion Metal Loss

### ILI Comparison: Box Matching and Signal Comparison

The 61 sized non-
      
      
      
      
      corrosion anomalies include 40 saved matches and 21 unmatched records. A signal-level decision on physical growth is not available; they are not reclassified as corrosion from depth differences alone.

### ILI Comparison: AutoSCAN

AutoSCAN was not included in the selected sco
      
      pe.

## Geometric Anomalies

The 196 current dents are included in the saved box-matching results summarised in Table 17.

Table 17: Comparison of Geometric Anomalies

| Anomaly Type | Total Number of Anomalies | Number Matched to Previous ILI | Number Not Matched to Previous ILI |
| --- | --- | --- | --- |
| Dents | 196 | 180 | 16 |
| ID Anomalies | 0 | 0 | 0 |
| Ovalities | 0 | 0 | 0 |
| Wrinkles | 0 | 0 | 0 |

Sixteen current dents have no saved previous match. This does not establish th
      
      at they 
      
      
      
      
      
      
      
      formed between inspections.

# FFP Assessment Summary

## Metal Loss Anomalies

Table 18 record
          
      s the saved whole-line assessment parameters. The OLD_FFP workbook also contains legacy input sheets; those inputs and its invalid time-to-repair cells have not been adopted as verified current-project calculations.

Table 18: Summary of the Key Assessment Parameters

| Pipeline Section | Start Log Distance | End Log Distance | Assessment Pressure [4] | Safety Factor |
| --- | --- | --- | --- | --- |
| Entire Section | Whole line | Whole line | 23.166 bar | 1.39; DNV 1.54 |
| No separate set | — | — | — | — |
| No separate set | — | — | — | — |

## Non-Metal Loss Anomalies

Table 19 retains the template methodology references for review; their inclusion does not confirm that all listed assessments have been completed
      .

Table 19: Non-Metal Loss Anomaly Assessment Summary

| Anomaly Type | Assessment Methodology | Relevant Section in ROSEN Standard Methodology Document for FFP and CGA Services [2] |
| --- | --- | --- |
| Dents | Depth based static, fatigue, strain | 3.1 |
| Ovalities | Screening to AS/NZS 2885.1 | 3.2 |
| Wrinkles / Buckles / Ripples | ASME B31.8 assessment criteria | 3.3 |
| Laminations | Screening to API 579 | 6 |

## CSA Z662 Compliance Summary

The supplied CSA Z662 compliance workbook has not been independently verified as part of this Box Matching with FFP draft.

# Metal Loss Integrity Assessment

## Immediate Integrity Assessment

Figure 13 presents the native Modified B31G corrosion assessment chart and saved OLD_FFP safe working pressures. The latter range from 35.551 to 128.231 bar, compared with the saved assessment pressure of 23.166 bar. These are saved outputs and have not been independently rec
      
      alcula
          
      
      
      
      
      
      
      ted.

Figure 13: Saved Corrosion Assessment Curve and Safe Working Pressure

T
      he immediate FFP export states “No immediate repairs”,
      
       and the current inspection summary reports no RSTRENG Effective Area FPR values of 1.0 or less. Confirm source-row identity, engineering inputs, sizing tolerance and repair treatment before accepting this conclusion.

Table 20: Immediate Investigation / Repair Summary

| Anomaly ID | Log Distance (m) | Event | Surface Location | Joint No. | Reported Depth (% wt) | Comment |
| --- | --- | --- | --- | --- | --- | --- |
| None listed | — | — | — | — | — | Saved export; acceptance pending. |
| — | — | — | — | — | — | — |
| — | — | — | — | — | — | — |

## Future Integrity Assessment

An illustrative five-year scenario applies the maximum positive Listing CGR, 0.633646 mm/ye
      ar, to all 8,331 current corrosion anomalies. The calculation uses an 80% wt depth limit and matching tally wall thickness, with reported depths and no added sizing tolerance.

The scenario yields 14, 17, 29, 89 and 190 depth-limit crossings in successive years 1–5 after the ILI, respectively (339 in total). Table 21 and Figure 14 show these screening results; they do not assign investigation or repair 
      
      
      
      
      
      
      
      d
      
      
      
      
      
      
      
      
      ates
      .

Table 21: Assumed Depth-Limit Crossings within Five Years of the 2026 ILI

| Anomaly Type | Anniversary Year after ILI |  |  |  |  |  |  | Total |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | n/a | n/a |  |
| Internal Corrosion | 0 | 0 | 0 | 0 | 0 | n/a | n/a | 0 |
| External Corrosion | 14 | 17 | 29 | 89 | 190 | n/a | n/a | 339 |
| Total | 14 | 17 | 29 | 89 | 190 | n/a | n/a | 339 |

Figure 14: Assumed Depth-Limit Crossings per Anniversary Year

# Geometric Integrity Assessment

## Immediate Integrity Assessment

The supplied dent dimensions and matching records suppor
      t the population summary. Static acceptance additionally requires validated geometry, weld interaction, associated damage and applicable assessment criteria.

Table 22 retains the template screening categories. Pending counts identify decisions that cannot be comple
      
      ted from the verified inputs.

Table 22: Geometric Anomalies; Immediate Assessment Results

| Anomaly Type | Assessment Criteria | Number of Anomalies | Action / Recommendation |
| --- | --- | --- | --- |
| Any Dent | Buried TOL | Pending | Determine risk of external interference damage and perform a gouging susceptibility study using ILI signal data and other complementary data sets. Monitor if low likelihood of external interference. If high likelihood, carry out a local targeted above-ground coating survey to determine the presence of any damage to the coating. Excavate if coating damage identified. Repair if excavation confirms associated mechanical damage. |
| Any Dent | L/d or W/d < 20 | Pending | Complete strain-based assessment or in-field investigation. |
| Dent Not Associated with Weld | >7% OD or Complex Geometry | Pending — — | Complete strain-based assessment or in-field investigation. |
| Dent On Weld | ≤2% OD | Pending — — | Consult records to confirm if weld is ductile. Repair if weld is brittle. |
|  | >2% OD or Complex Geometry | Pending — — | Consult records to confirm if weld is ductile. Repair if weld is brittle. Complete strain-based assessment or in-field investigation. |
| Dent with Corrosion | Corrosion >40% wt or not acceptable according to metal loss assessment | Pending — — | Investigate in-field and repair if: Associated mechanical damage confirmed. Corrosion confirmed as unacceptable. |
| Dent with Possible Mechanical Damage | Any | Pending — — | Investigate in-field and repair if associated mechanical damage confirmed. |
| Ovality | Min ID <95% Nominal ID or in an area of instability | 0 reported | Assess further to determine significance on the immediate and future integrity of the pipeline or in-field investigation. |
| Buckle | Any | 0 reported | Assess further to determine significance on the immediate and future integrity of the pipeline or in-field investigation. |
| Bulge | Any | 0 reported | Assess further to determine significance on the immediate and future integrity of the pipeline or in-field investigation. |
| Enlargement | Any | 0 reported | Assess further to determine significance on the immediate and future integrity of the pipeline or in-field investigation. |
| Wrinkle / Ripple | Exceeds allowable height limit, interacts with metal loss or weld or located in area of instability | 0 reported | Assess further to determine significance on the immediate and future integrity of the pipeline or in-field investigation. |

Static and fatigue acceptance remain separate decisions. A pressure-cycle history is required for a fatigue assessment.

A final geometric investigation or repair list cannot be issued until the pending assessment decisions are resolved
      .

## Fatigue Assessment

Fatigue lives for the 196 reported dent
      s have not been established. No validated pressure time series was supplied
      
      .

No dent fatigue-b
      a
      
      
      
      
      
      
      sed r
      epair schedule is assigned.

Any future fatigue assessment must address associated cracking or gouging and the validity of its geometry and stress assumptions.

Following verification, the final geometric findings should be incorporated into the investigation or repair listing.

# Lamination Integrity Assessment

## Immediate Integrity Assessment

The supplied API 579 lamination workbook contains 30 records, but through-thickness dimensions T1 and T2 are missing
      
       for every
          
       record.

Cached surface-breaking and failure flags cannot be accepted as assessment findings until the missing dimensions and interaction mappings are verified.

Table 23: Lamination Assessment Results

| Assessment Criteria | Number of Laminations | Actions / Recommendations |
| --- | --- | --- |
| Sloping/Surface Breaking | Pending | Assess as crack-like flaws. API 579 requires that all surface‑breaking or sloping laminations are assessed as crack‑like flaws. |
| Associated with Welds and/or Major Structural Discontinuities | Pending | Desk‑Based Loading Review: Irving Oil should confirm whether axial loading is a credible threat at lamination locations. Where no threat exists, further action is generally unnecessary. Targeted Investigation Where Needed: If axial loading is identified as a potential concern, further review of crossings, existing mitigation, and geotechnical factors may be required. Field investigation should be focused on locations with the highest susceptibility. |
| Laminations with Metal Loss | Pending | Metal loss interaction counts are not established from the supplied screening inputs. Confirm the metal loss dimensions, surface and association before combined-flaw assessment. |

Static acceptance and
       fatigue assessment remain unresolved for the laminations.

A final lamination investigation list requires verified classifications and completed assessments
      .

## Crack Assessment

Selection of laminations for crack-like flaw assess
      ment requires verified geometry and surface-breaking or sloping classification
      .

No independently verified crack-
      assessment acceptance or failure count is available.

## Fatigue Assessment

A lamination
      
       fatigue assessment 
      requires validated loading, materi
      al and crack geometry inputs and a pressure history.

No lamination fatigue-based repair date
      
      
      
      s are assigned
      .

# Other Integrity Related Issues

## Close Metal Objects

The tally contains 99 possible installations but does not explicitly classify them as close metal objects (CMOs).

A
      
      
       CMO
      
      
      
      
      
      
      
      
      
      
      
      
      
      
      
      
      
      
      
      
      
      
      
      
      
       proximity count and associated action list require confirmed installation classifications. Do not infer a CMO threat or its absence from the “Possible Installation” label alone.

## Eccentric Casings

No eccentric casings are identified in the supplied summary. Any casing records should be reviewed separately for coating or cathodic-protection interference
      .

Where a casing is confirmed, review corrosion and
      
      
      
      
      
      
      
      
      
      
      
      
      
      
       mitigation using the verified casing limits and anomaly associations. Potential measures include:

Check the integrity of the casing end seals and for evidence of water ingress.

If possible, remove any water from the casing annulus and/or inert with corrosion inhibitors (typical inhibitors for use within a casing annulus are vapour inhibitors or gel inhibitors).

Seal the casing ends preventing further water ingress.

Monitor corrosion rates u
      sing an appropriate validated monitoring method.

Determine inspection timing from the completed engineering assessment.

It is also recommended that Irving Oil monitor all eccentric casings for any further external corrosion activity in future ILIs.

## Half Sleeves / Patch Repairs

T
      he tally identifies 21 patch installations. Confirm their construction, condition and applicable code requirements, including the following information:

Half shells and patches were permitted according to the applicable local pipeline code and any other regulations.

Appropriate qualified weld procedures were followed.

The absence of any defects was confirmed using Non-Destructive Testing (NDT).

A Stress-Endurance (SN) fatigue assessment of the fillet welds has been conducted and demonstrated to have an acceptable fatigue life.

For confirmed patch or sleeve repairs whose construction, condition or compliance remains unresolved, determine appropriate inspection requirements. If damage or cracking is detected, determine the required response through an engineering assessment using the governing code and a verified repair design.

Reported repair-installation records include 21 patches, 36 sleeve start/end pairs and one separate Sleeve event. Reconcile the separate event with the paired records before assigning a total physical sleeve count. Installation presence does not demonstrate repair adequacy or resolve the status of individual anomalies
      .

## Weld Overlays

N
      o weld overlays are identified in the supplied summary. Review any separately confirmed weld-deposition repairs for welding and inspection compliance.

If a weld-deposition repair is confirmed, establish whether qualified welding procedures and appropriate inspection were used.

Irving Oil should verify the applicable welding and inspection records for any such confirmed repair.

## Closely Spaced Sleeves

The templat
      e sleeve guidance should be checked against the governing code edi
      
      tion and actual repair design before it is applied to this pipeline.

A verified count of closely spaced sleeves is not yet established from the supplied installation records.

For any confirmed closely spaced sleeves, establish whether a bridging sleeve or continuous construction is present
      
      . The following records and loading review may be required:

Repair records in relation to the closely spaced sleeves should be checked to confirm the presence of bridging sleeves.

If a bridging sleeve has not been installed or this cannot be confirmed, Irving Oil should give due consideration to the cyclic loads due to axial, thermal and pressure cycling which may be present at the locations in order to determine the risk of crack growth due to the ‘notch-like’ condition.

In those parts of the pipeline where the risk of crack growth is considered to be high due consideration should be given to the installation of a bridging sleeve.

## Mitre Bends

N
      o mitre bends are identified in the supplied summary. If any are confirmed separately, review the relevant geometry, welding and cyclic loading, including:

Potential weld defects due to the difficulty of welding mitred joints.

Difficulty of detecting any weld defects.

Bending movement induced on the bend due to axial component of internal pressure.

All of the above are exacerbated by pressure and / or thermal cyclic loading.

Table 24 retains the example ASME B31.4 
      guidance for reference. Confirm the applicable code text, edition and project requirements before using it.

Table 24: ASME B31.4 Mitre Bend Guidance

| Operational Hoop Stress | Guidance Summary |
| --- | --- |
| <10% SMYS | Acceptable with no restriction. |
| ≥10% and ≤20% SMYS | Acceptable with the following restrictions: Angle <12.5°, and Minimum distance between mitres (measured at the crotch) is not <1 OD |
| >20% SMYS | Not Acceptable |

No project-specific mitre-bend
       complianc
      e conclusion is mad
      e fro
      m the supplied record
      s
      .

Confirm the governing design code and drawings for any subsequently identified mitre bends.

## Illegal Offtakes

The tally records 72 taps. It does not identify an
       illegal or suspicious offtake classification
      
      .

R
      eview design, installation and maintenance records before classifying any connection as an illegal offtake
      
      
      .

# Integrity Management Summary

## Mitigation Strategy

The integrity management summary combines verified reported observations with explicitly identified screening assumptions 
      
      and unresolved enginee
      
      ring decisions.

### Internal Corrosion

No internal corrosion anomalies are reported. This does not establish zero future internal corrosion growth.

### External Corrosion

External corrosion is the dominant reported metal loss population. Review the saved historical CGRs with coating, cathodic protection, repair and inspection-quality information before selecting recommended 
      
      
      gr
      
      
      
      ow
      
      
      th rates.

## Repair Plan

Table 25 and Figure 15 present the same assumed depth-limit scenario as Section 5.2. The 339 crossings are screening results, not an approved
      
      
       repair plan; non-corrosion, dent and lamination repair decisions are not established.

Table 25: Assumed Five
      
      -Year Depth-Limit Scenario

| Anomaly Type | Anniversary Year after ILI |  |  |  |  |  | Total |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | At ILI | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 |  |
| Internal Corrosion | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| External Corrosion | 0 | 14 | 17 | 29 | 89 | 190 | 339 |
| Non-Corrosion Metal Loss Anomaly | — | — | — | — | — | — | — |
| Geometric Anomaly | — | — | — | — | — | — | — |
| Lamination | — | — | — | — | — | — | — |
| Scenario total (corrosion) | 0 | 14 | 17 | 29 | 89 | 190 | 339 |

Figure 15: Assumed Depth-Limit Crossing Time versus
      
       Log Distance

### Sectional Repair Plan

A sectional repair plan requires verified anomaly acceptance, repair status and investigation priorities. The scenario alone does not determine sleeve or replacement locations.

If a 1.22 m Type B sleeve is used as a preliminary planning assumption, confirm its applicability and design before estimating repair quantities.

No
      
       mobilisation or grouped-repair count is inferred from the scenario.

## Reinspection and Reassessment

This section considers the evidence needed to select future ILI timing and appropriate tool technology. No recommended reinspection interval has been established. Interval selection requires completion of the corrosion assessment and consideration of inspection needs for other relevant threats, including geometric deformation and pipeline movement.

The scenario do
      es not establish
      
      
      
       a safe reinspection interval. Complete the future-integrity assessment using validated rates, tolerances, interactions and repair treatment before selecting the interval.

Future ILI should use compatible UT wall measurement and geometry technolog
      
      ies to support comparison with the current inspection.

Review the interval and mitigation whenever field findings or monitoring indicate growth or damage beyond the assumptions used in the assessment
      
      .

If field investigations or monitoring indicate growth beyond the assumed scenario rate or otherwise invalidate its assumptions, review the growth-rate basis and repeat the relevant assessment. Establish any investigation or repair schedule and reinspection interval through the completed engineering assessment. The 80% depth-limit scenario is not an approved FFP repair schedule.

# References

| [1] | Project proposal / agreed service scope: not supplied. |
| --- | --- |
| [2] | ROSEN Standard Methodology Document for FFP and CGA Services, Rev. 2026_0: cited by the template; applicable controlled copy to be confirmed. |
| [3] | ROSEN, “NPS 24 Refinery to Dock #1 Bunker Pipeline”, UTWM-GEO-IMU final inspection report, project 0-1001-18338, Rev. 0, August 14, 2026; survey May 21, 2026. |
| [4] | Pipeline questionnaire included in the 2026 final inspection report, physical pages 13–16; revision April 13, 2026. |
| [5] | ROSEN, “NPS 24 Refinery to Dock #1 Bunker Pipeline”, final inspection report, project 0-1001-15621, Rev. 0, December 7, 2020; surveys October 7–8, 2020. |
| [6] | American Society of Mechanical Engineers, “ASME B31.4 Pipeline Transportation Systems for Liquids and Slurries,” December 2022. |

Scope of Work

This draft addresses the user-selected Box Matching with FFP scope. Confirm the contractual scope and applicable
      
      
           methodology documents before release
          .

- Review the ILI data and provide a breakdown of the main anomalies relevant to the study (anomaly distribution, changes in pipe characteristics, repairs / replacements, etc.).

Review the ILI data along with other available pipeline survey data (product data, cathodic protection data etc.) to identify the likely corrosion mechanisms.

Conduct a distance and joint number correlation to align the 2 ILI data sets.

Compare the recent and previous anomaly lists using proprietary box matching software.

Based on the box matching results, make an initial estimate of the historical CGR for each corrosion anomaly reported by the recent ILI (based on reported depths).

Paired signal-comparison examples require the corresponding raw inspection signal exports.

For the anomalies included in the signal comparisons, identify any evidence (or otherwise) of corrosion growth and update the historical CGRs where appropriate.

Split the pipeline into segments using a semi‑automated segmentation process (note, a unique segmentation will be produced for internal and external corrosion), based on the results of:

- DBSCAN – Used to split the reported corrosion anomalies into ‘concentrations’ and isolated, less dense areas of corrosion (‘noise’).

- Pipe Tally Analysis – Review of the ILI pipe tally / design construction data to identify changes in pipe parameters that may impact corrosion susceptibility.

Recommend a characteristic CGR to be assigned to the corrosion anomalies in each defined segment.

Identify any other changes in the pipeline, e.g. dents introduced between the 2 ILI runs. This is limited to identifying new geometric anomalies and does not aim to identify/rule out any change in deformation shape.

Assess the significance of the corrosion anomalies and any other metal loss anomalies reported in the pipeline, at a pre-agreed assessment pressure.

Identify any anomalies requiring remediation in accordance with relevant industry guidance at the time of the recent ILI.

Future investigation and repair planning remains subject to completion of the verified assessment; the present five-year result is the labelled depth-limit scenario.

Identify an appropriate reinspection interval.

Document the findings in a written report and spreadsheet listing.

e.g. kinked / multi-apex / double dents / off-axis

Table 5 uses the full reported inspection populations. Figu
      re 8 uses the available previous matched subset. No separate pre- and post-clustering counts are assigned.

Matched and unmatched labels refer to saved previous Feature IDs. Repeated previous IDs do not establish an approved representative-anomaly selection.

Signal-level new-growth classifications are unavailable because paired raw
       signal evidence was not supplied
      .

Saved numeric historical rates retain their original signs. Missing rates are not converted to zero; no signal-based zero-rate assignment is made.

Matched and unmatched labels refer to saved previous Feature IDs. Repeated previous IDs do not establish an approved representative-anomaly selection.

Signal-level new-growth classifications are unavailable because paired raw signal evidence was not supplied.

Saved numeric historical rates retain their original signs. Missing rates are not converted to zero; no signal-based zero-rate assignment is made.

The immediate FFP workbook saves factors of 1.39 for non-DNV methods and 1.54 for DNV. These are recorded source parameters, not confirmation of assessment-method applicability.

The 196 current dent records retain their Listing classification. No additional ID anomalies have been converted to dents.

e.g. curvature strain / FEA based Level 3 assessment using Strain Limiting Damage / Ductile Failure Damage Indicator

e.g. kinked / multi-apex / double dents / off axis

e.g. curvature strain / FEA based Level 3 assessment using Strain Limiting Damage / Ductile Failure Damage Indicator

e.g. kinked / multi-apex / double dents / off axis

e.g. curvature strain / FEA based Level 3 assessment using Strain Limiting Damage / Ductile Failure Damage Indicator

e.g. areas of bending strain, pipeline movement or unstable ground

e.g. areas of bending strain, pipeline movement or unstable ground.